May 21, 2006

Abraham Murra

Project Manager, CSA B483

Canadian Standards Association

5060 Spectrum Way, Ste 100

Mississauga, Ontario L4W 5N6

Canada

Dear Mr. Murra:

The Association of Home Appliance Manufacturers (AHAM) is a U.S. based trade association representing the manufacturers of home appliances, and suppliers to the industry.  This includes the manufacturers of refrigerator-freezers, and component suppliers.  We appreciate the opportunity to provide our comments on draft standard CSA B483.1, Drinking water treatment systems.

AHAM supports CSA in its efforts to ensure that safe drinking water is provided to consumers, and we are committed to assisting in this effort as necessary.  AHAM has held a series of meetings with its Refrigerator-Freezer Specialists and we have developed the following comments on the draft standard.

Manufacturers belonging to AHAM have a long history of providing safe drinking water systems as part of refrigerator-freezers that incorporate water dispensing systems and ice maker systems.  Refrigerator-freezer manufacturers have shipped tens of millions of units with water dispensing systems, and they report there is no history of any health related problems with water treatment.

The primary component in refrigerator water treatment systems is the water filter, which is certified to be in compliance with NSF/ANSI standards 42, 53 and 61.  Other materials used in refrigerators also comply with the requirements of the United States Food and Drug Administration with respect to contact to food and water, per 21 CFR Part 177.  There are also additional requirements in the U.S. Safe Drinking Water Act.

The above requirements are sufficient to ensure safe drinking water from refrigerator systems, as evidenced by the fact that there is no history of any health related problems.  Therefore, there is no need to place additional conformity assessment burden on the manufacturers of refrigerators.

Therefore, we respectfully request that the scope of draft standard B483.1 be clarified to indicate that this standard does not apply to refrigerators-freezers or ice makers.

Some refrigerators have water dispensing systems, but they do not contain any water treatment components, such as a water filter.  Under the current scope, units that are manufactured with filters would have to be tested according to B483.1, whereas units with no filter, but with the same components as filtered units, would not have to be tested.  This doesn’t make sense because the components of the two units, with the exception of the presence of a filter, are identical. The components of the unit with the filter should not be subjected to additional requirements just because they are used in a unit with a filter, when components used in the unit without the filter would not be covered by the standard.

In the event that the CSA committee does not agree to exempt refrigerator-freezers from B483.1, AHAM would like to go on record as supporting the comments submitted by the Canadian Water Quality Association (CWQA), and we offer additional comments as outlined below.

1.  Pressure and Extraction Requirements (Clauses 4.1.1 and 4.2.2):

It appears that the standard would require 500 psi pressure be applied to the entire system, and that the NSF 42 extraction test be applied to the entire system.  These requirements are presently applied only to the water filter.  Adding these requirements to the whole system would add unnecessary cost, as well as test burden.  Indeed, as there is no evidence of any problems associated with pressure or extraction concerns with other components in the system, this standard would add cost to correct a nonexistent problem.

If this standard does expand to include the entire system then it seems logical to only include the components that actually see line pressure.  There are parts in the water system that see much lower pressure per design intent.  For example, the water valve sees line pressure where some components down stream see significantly lower pressure.

2.  Structural Requirements (Clause 4.2):

There are several structural tests that would be applied to the water system.  The spigot on the in-door ice and water would be treated like a faucet and would require a 10,000 cycle test to pass the requirements in the standard.   Under the standard, 100 psi water pressure would be applied to the system, or pressure as recommended by the manufacturer, whichever is more rigorous.  The valves would require a 100,000 cycle test under the same condition.  The check valve would require a 200 cycle test.

The above tests are reliability requirements for components that would have no bearing on providing safe drinking water.  Therefore, they should be removed from the standard since they are not applicable to a safe drinking water standard.

3.  Backflow Prevention (Clause 4.6):

There is a section in the standard that requires a backflow prevention test.  It is unclear how this requirement would apply to refrigerator-freezers.  Historically the air gap between the ice-maker water fill tube and the ice-maker overflow has been viewed as sufficient protection against backflow.  The water dispenser is no different than a water faucet, and water in the line is not contaminated.  AHAM members report that harmful bacteria do not grow in this line.  A check valve before the water system should not be required, since there is a solenoid valve.  This area of the standard needs clarification.

4.  Solenoid Valves (Clause 4.3.5):

Solenoid valves should not be included since this standard deals with safe drinking water, not reliability issues of mechanical components.  The functioning of a solenoid valve has no bearing on providing safe drinking water.

5.  Thermal Cycle & Hydrostatic Pressure Test for Faucet End Point Devices (Clause 5.3):

This requirement should not apply to refrigerators and refrigerator-freezers due to low pressure at the outlet and water temperatures between 34 °F to 40 °F.

6.  Marking and Documentation (Clause 6):

Filters used in refrigerators are already marked in compliance with the appropriate NSF standards.  With the exception of the water filter, the components in contact with water on a refrigerator-freezer are hidden from view and therefore it would not be practical to mark them.  There should be no additional marking requirements for refrigerator-freezers.  In order to easily identify units that are in compliance with B483, a statement of compliance could be included in the product literature if necessary.

Thank you for your consideration of our comments.  Please feel free to contact me if you have any questions.  We would also like to attend the next meeting of the CSA B483.1 committee.

Sincerely,

Lawrence R. Wethje, P.E.

Vice President Technical Services